Hi Delta SS® TYPE H - MODELS HD151 – HD401
SUGGESTED SPECIFICATIONS

Part Number:	 100-10000170 Rev. 02

Effective:        02-13-2025

Replaces:       07-29-2022

### DIVISION 23 52 33.13

### FINNED WATER-TUBE BOILERS

- GENERAL

SUMMARY

Section includes gas-fired, copper finned-tube hydronic heating boilers.

Related Sections

Specifier Note:  Use as needed

Building Services Piping – Division 23 21 00

Breeching, Chimneys, and Stacks (Venting) – Division 23 51 00

HVAC Instrumentation and Controls – Division 23 09 00

Electrical – Division 23 09 33

REFERENCES

ANSI Z21.13/CSA 4.9

ASME, Section IV

2006 UMC, Section 1107.6

ANSI/ASHRAE 15-1994, Section 8.13.6

National Fuel Gas Code, ANSI Z223.1/NFPA 54

I=B=R

NEC

ASME CSD-1, 2018 (when required)

SUBMITTALS

Product data sheet (including dimensions, rated capacities, shipping weights, accessories)

Wiring diagram

Warranty information

Installation and operating instructions

QUALITY ASSURANCE

Regulatory Requirements

ANSI Z21.13/CSA 4.9

Local and national air quality regulations for low NOx (0-20 PPM NOx emissions) boilers

Certifications

CSA

ASME H-Stamped and National Board registered

WARRANTY

Limited one-year warranty from date of installation

Limited twenty-year thermal shock warranty

Limited ten-year closed-system heat exchanger warranty

- PRODUCTS

MANUFACTURER

Raypak, Inc.

Contact: 2151 Eastman Ave., Oxnard, CA 93030; Telephone: (805) 278-5300; 
Website: www.raypak.com

Product: Hi Delta SS® copper finned-tube hydronic boiler(s)

BOILERS

General

The boiler(s) shall be fired with                 gas at a rated input of               BTU/hr.

The boiler(s) shall be CSA tested and certified with a minimum thermal efficiency of 84% at full fire.

The boiler(s) shall be ASME inspected, stamped and National Board registered for 160 PSIG maximum working pressure, complete with a Manufacturer's Data Report.

The boiler(s) shall have a floor loading of 45 lbs. / square foot or less.

Heat Exchanger

The heat exchanger shall be of a single-bank, horizontal-grid design with nine integral copper finned tubes, each end of which is rolled into an ASME boiler quality steel tube sheet.

The heat exchanger shall be sealed to 160 PSIG rated cast iron headers with high-temperature silicone O-ring gaskets.

The low water volume heat exchanger shall be explosion-proof on the water side and shall carry a twenty-year warranty against thermal shock.

The headers shall be secured to the tube sheet by stud bolts with flange nuts to permit inspection and maintenance without removal of external piping connections.

The boiler(s) shall be capable of operating at inlet water temperatures as low as 105°F without condensation.

Burners

The tubular burners shall have gas orifices, punched ports and slots, be capable of quiet

- ignition and extinction without flashback at the orifice, and be manufactured from corrosion resistant, stainless steel with low expansion coefficient.

The burners will be supplied with a fan-assisted, clean-burning, and highly efficient fuel-air mixture.

Ignition Control System

The boiler(s) shall be equipped with a 100% safety shutdown system.

The ignition shall be Hot Surface Ignition (HSI) type with full-flame rectification by remote sensing separate from the ignition source, with a three try-for-ignition sequence, to ensure consistent operation.

The igniter will be located away from the water inlet to protect the device from condensation during startup.

An external viewing port shall be provided, permitting visual observation of burner operation.

Gas Train

The boiler(s) shall have dual-seated main gas valve(s).

Gas control trains shall have a redundant safety shut-off feature, main gas regulator, and plugged-pressure tapping to meet the requirements of ANSI Z21.13/CSA 4.9.

Boiler Control

The following safety controls shall be provided:

High limit control

Flow switch

PSIG ASME pressure relief valve, piped by the installer to an approved drain

Temperature and pressure gauge

The boiler(s) shall be equipped with an energy-saving pump relay, mounted and wired, which automatically shuts off the boiler pump at a set period after boiler shut-down (adjustable for two settings of five or ten minutes) to avoid standby losses associated with constant pump operation.

Firing Mode

Models HD151–HD401, provide two-stage fire control of the gas input to the boiler (on/off fire optional).

Boiler Diagnostics

Provide internal LED displaying the following boiler status/faults:

Steady on – Internal control failure

One flash – Air flow fault

Two flashes – Erroneous flame signal

Three flashes – Ignition lockout

Combustion Chamber: The lightweight, high-temperature, multi-piece, interlocking ceramic fiber combustion chamber liner shall be sealed to reduce standby radiation losses, reducing jacket losses and increasing unit efficiency.

Venting

When routed vertically, the boiler’s flue material and size shall be in accordance with the National Fuel Gas Code, ANSI Z223.1/NFPA 54 latest edition (Category I).

When routed horizontally, the boiler(s) flue material and size shall meet or exceed the requirements as specified for Category III in the National Fuel Gas Code, ANSI Z223.1/NFPA 54 latest edition.

The boiler(s) shall be TruSeal® direct vent ready. The boiler(s) shall meet safety standards for direct vent equipment as noted by: the 2006 UMC Section 1107.6; ASHRAE 15-1994, Section 8.13.6; and ANSI Z21.13/CSA 4.9.

Cabinet

The corrosion-resistant galvanized steel jackets shall be finished with a baked-on epoxy powder-coat which is suitable for outdoor installation, applied prior to assembly for complete coverage, and shall incorporate louvers in the outer panels to divert air past heated surfaces.

The boiler(s), if located on a combustible floor, shall not require a separate combustible floor base.

Combustion air intake shall be on left side of the cabinet.

Specifier Note:	The remaining items in this section are options. Delete those that are not being specified.

Boiler Operating Controls

The boilers(s) shall feature an integral controller for sizes HD151-HD301 (optional on size HD401 only).

Boiler Pump - Refer to Equipment Schedule

Cold Water Run System

The boiler(s) shall be configured with a cold water run automatic proportional bypass system that ensures the boiler will experience inlet temperatures in excess of 105ºF within 7 minutes to avoid damaging condensation.

The cold water run system shall be configured with a variable-speed pump that is controlled by a system-matched PID control that injects the correct amount of cold water directly into the boiler loop to maintain a minimum inlet temperature. The PID controller temperature sensor shall be located in the inlet header of the boiler.

The control shall have temperature setting DIP switches located on the face of the board. The PID Logic shall be capable of limiting system overshoot on initial start-up or call-for-heat.

The cold water run system shall be shipped loose for field installation.

SOURCE QUALITY CONTROL

The boiler(s) shall be completely assembled, wired, and fire-tested prior to shipment from the factory.

The boiler(s) shall be furnished with the sales order, ASME Manufacturer’s Data Report, inspection sheet, wiring diagram, rating plate and Installation and Operating Manual.

- EXECUTION

INSTALLATION

Must comply with:

Local, state, provincial, and national codes, laws, regulations and ordinances

National Fuel Gas Code, ANSI Z223.1/NFPA 54 – latest edition

National Electrical Code, ANSI/NFPA 70 – latest edition

Canada only: CAN/CSA B149 Installation Code and CSA C22.1 CEC Part I

Manufacturer’s installation instructions, including required service clearances and venting guidelines

Manufacturer’s representative to verify proper and complete installation.

START-UP

Shall be performed by Raypak factory-trained personnel.

Test during operation and adjust if necessary:

Safeties

Operating Controls

Static and full-load gas supply pressures

Gas manifold and blower air pressures

Submit copy of start-up report to Architect and Engineer.

training

Provide factory-authorized service representative to train maintenance personnel on procedures and schedules related to start-up, shut-down, trouble shooting, servicing, and preventive maintenance.

Schedule training at least seven days in advance.

- END OF SECTION