Part Number:	 242009 Rev. 2

Effective:	02-01-2025

Replaces:	11-25-2021

Hi Delta SS®, TYPE WH - MODELS HD151 – HD401
SUGGESTED SPECIFICATIONS

### DIVISION 23 52 33.13

### FINNED WATER-TUBE WATER HEATERS

- GENERAL

SUMMARY

Section includes copper or cupronickel finned-tube, gas-fired water heaters for use with or without a storage tank.

Related Sections

Specifier Note:  Use as needed

Building Services Piping – Division 23 21 00

Breeching, Chimneys, and Stacks (Venting) – Division 23 51 00

HVAC Instrumentation and Controls – Division 23 09 00

Electrical – Division 23 09 33

REFERENCES

ANSI Z21.10.3/CSA 4.3

ASME, Section IV

2006 UMC, Section 1107.6

ANSI/ASHRAE 15-1994, Section 8.13.6

National Fuel Gas Code, ANSI Z223.1/NFPA 54

NEC, ANSI/NFPA 70

ASME CSD-1, 2018 (when required)

SUBMITTALS

Product data sheet (including dimensions, rated capacities, shipping weights, accessories)

Wiring diagram

Warranty information

Installation and operating instructions

QUALITY ASSURANCE

Regulatory Requirements

ANSI Z21.10.3/CSA 4.3

Local and national air quality regulations for low NOx (0-20 PPM NOx emissions) water heaters

Certifications

CSA

ASME HLW-Stamped and National Board registered

CSA-Certified – Low-Lead Compliant

WARRANTY

Limited one-years parts warranty

Limited five-year warranty from date of installation

Limited five-year copper heat exchanger warranty

Limited ten-year cupronickel heat exchanger warranty

Limited twenty-year thermal shock warranty

- PRODUCTS

MANUFACTURER

Raypak, Inc.

Contact: 2151 Eastman Ave., Oxnard, CA 93030; Telephone: (805) 278-5300; 
Website: www.raypak.com

Product: Hi Delta SS copper or cupronickel finned-tube water heater(s)

WATER HEATERS

General

The water heater(s) shall be fired with                 gas at a rated input of               BTU/hr.

The water heater(s) shall be CSA tested and certified with a minimum thermal efficiency of 85% for copper (83% for cupronickel) finned tubes.

The water heater(s) shall be ASME inspected and HLW-stamped and National Board registered for 160 PSIG maximum working pressure, complete with a Manufacturer's Data Report.

The water heater(s) shall have a floor loading of 45 lbs. /square foot or less.

Heat Exchanger

The heat exchanger shall be of a single-bank, horizontal-grid design with nine integral copper or cupronickel finned-tubes, each end of which is rolled into an ASME water heater quality steel tube sheet.

The heat exchanger shall be sealed to 160 PSIG rated bronze headers with high-temperature silicone O-ring gaskets.

The low water volume heat exchanger shall be explosion-proof on the water side and shall carry a twenty-year warranty against thermal shock.

The headers shall be secured to the tube sheet by stud bolts with flange nuts to permit inspection and maintenance without removal of external piping connections. The heat exchanger shall incorporate "V” baffles between the tubes to ensure complete contact of the external tube surfaces with the products of combustion.

The water heater(s) shall be capable of operating at inlet water temperatures as low as 105°F without condensation.

The heat exchanger shall be AB-1953 compliant in construction and verification by a third-party certification agency.

Burners

The tubular burners shall have multiport radial gas orifices, punched ports and slots, be capable of quiet-ignition and extinction without flashback at the orifice, and be manufactured from corrosion-resistant, titanium-stabilized stainless steel with low-coefficient of expansion.

The burners will be supplied with a fan-assisted, clean-burning, and highly efficient fuel-air mixture.

Ignition Control System

The water heater(s) shall be equipped with a 100% safety shutdown system.

The ignition shall be Hot Surface Ignition (HSI) type with full-flame rectification by remote sensing separate from the ignition source, with a three try-for-ignition sequence, to ensure consistent operation.

The igniter will be located away from the water inlet to protect the device from condensation during startup.

An external viewing port shall be provided, permitting visual observation of burner operation.

Gas Train

The water heater(s) shall have dual-seated main gas valve(s).

Gas control trains shall have a redundant safety shut-off feature, main gas regulator, and plugged-pressure tapping to meet the requirements of ANSI Z21.10.3/CSA 4.3.

Water Heater Control

The following safety controls shall be provided:

High limit control

Flow switch

PSIG ASME pressure relief valve, piped by the installer to an approved drain

Temperature and pressure gauge

The water heater(s) shall be equipped with an energy-saving pump relay, mounted and wired, which automatically shuts off the water heater pump at a set period after water heater shut-down (adjustable for two settings of five or ten minutes) to avoid standby losses associated with constant pump operation.

Firing Mode

Models HD151–HD401, provide on/off control of the gas input to the water heater.

Water Heater Diagnostics

Provide internal LED displaying the following water heater status/faults:

Steady on – Internal control failure

One flash – Air flow fault

Two flashes – Erroneous flame signal

Three flashes – Ignition lockout

Combustion Chamber: The lightweight, high-temperature, multi-piece, interlocking ceramic fiber combustion chamber liner shall be sealed to reduce standby radiation losses, reducing jacket losses and increasing unit efficiency.

Venting

When routed vertically, the water heater’s flue material and size shall be in accordance with the National Fuel Gas Code, ANSI Z223.1/NFPA 54 latest edition (Category I).

When routed horizontally, the water heater(s) flue material and size shall meet or exceed the requirements as specified for Category III in the National Fuel Gas Code, ANSI Z223.1/NFPA 54 latest edition.

The water heater(s) shall be TruSeal™ direct vent ready. The water heater(s) shall meet safety standards for direct vent equipment as noted by: the 2006 UMC Section 1107.6; ASHRAE 15-1994, Section 8.13.6; and ANSI Z21.10.3/CSA 4.3.

Cabinet

The corrosion-resistant galvanized steel jackets shall be finished with a baked-on epoxy powder-coat which is suitable for outdoor installation, applied prior to assembly for complete coverage, and shall incorporate louvers in the outer panels to divert air past heated surfaces.

The water heater(s), if located on a combustible floor, shall not require a separate combustible floor base.

Combustion air intake shall be on left-side of the cabinet.

Specifier Note:	The remaining items in this section are options. Delete those that are not being specified.

Water Heater Operating Controls

The water heaters(s) shall feature an optional controller.

High and low gas pressure switch (optional – factory installed)

Water Heater Pump - Refer to Equipment Schedule

Cold Water Run System

The water heater(s) shall be configured with a cold water run automatic proportional bypass system that ensures the water heater will experience inlet temperatures in excess of 105ºF within 7-minutes to avoid damaging condensation. The unit will automatically shut down if the inlet temperature is not achieved within the 7-minute time frame.

The cold water run system shall be configured with a variable-speed pump that is controlled by a system-matched PID control that injects the correct amount of cold water directly into the water heater loop to maintain a minimum inlet temperature. The PID controller temperature sensor shall be located in the inlet header of the water heater.

The control shall have a temperature setting dial located on the face of the board. The temperature range of the dial shall be 105ºF to 120ºF. The PID Logic shall be capable of limiting system overshoot to a maximum of 10ºF on initial start-up or call-for-heat.

The cold water run system shall be completely wired and mounted at the factory.

The control shall have the following diagnostic LEDs:

Call-for-heat

Start-up mode

Inlet temperature error

Sensor out-of-range

The controller shall have alarm contacts.

SOURCE QUALITY CONTROL

The water heater(s) shall be completely assembled, wired, and fire-tested prior to shipment from the factory.

The water heater(s) shall be furnished with the sales order, ASME Manufacturer’s Data Report, inspection sheet, wiring diagram, rating plate and Installation and Operating Manual.

- EXECUTION

INSTALLATION

Must comply with:

Local, state, provincial, and national codes, laws, regulations and ordinances

National Fuel Gas Code, ANSI Z223.1/NFPA 54 – latest edition

National Electrical Code, ANSI/NFPA 70 – latest edition

Canada only: CAN/CSA B149 Installation Code and CSA C22.1 CEC Part I

Manufacturer’s installation instructions, including required service clearances and venting guidelines

Manufacturer’s representative to verify proper and complete installation.

START-UP

Shall be performed by Raypak factory-trained personnel.

Test during operation and adjust if necessary:

Safeties (2.2 - F)

Operating Controls (2.3)

Static and full-load gas supply pressures

Gas manifold and blower air pressures

Submit copy of start-up report to Architect and Engineer.

training

Provide factory-authorized service representative to train maintenance personnel on procedures and schedules related to start-up, shut-down, trouble shooting, servicing, and preventive maintenance.

Schedule training at least seven days in advance.

- END OF SECTION