## Lines
Line Type | Description | Answer | Value | Note | Allow N/A | Prompt For Issue | Issue Preset | Linked Attribute | Units | Title | Options | Include None Of The Above | Labels | Display
Header | Documentation
File | Are manufacturer's cut sheets submitted? | Passed |  |  | Allow | Prompt | Missing Documentation
File | Is performance data (fan curves, coil data, etc.) submitted? | Passed |  |  | Allow | Prompt | Missing Documentation
File | Is installation and startup manual and plan submitted? | Passed |  |  | Allow |  | Missing Documentation
File | Is Test and Balance report submitted? | Passed |  |  | Allow |  | Missing Documentation
Header | Model Verification
Attribute | Record Serial Number: | Passed | X1234 |  | Allow |  |  | Serial Number
Attribute | Record Capacity: | Passed | 100 |  | Allow |  |  | Capacity | kW
Information | Installation
Multiple Value | Are permanent labels affixed, including for fans? | Passed | Unit labeled ¦ Fan labeled |  | Allow | [5 empty] | Unit labeled ¦ Fan labeled | Include |  | Select
Single Value | Is casing condition good: no dents, leaks, door gaskets installed? | Passed | New |  | Allow | Prompt |  |  |  |  | New: Passed ¦ Good: Passed ¦ Poor: Passed ¦ Replace: Failed |  |  | Select
Standard Question | Are access doors close tightly - no leaks? | Passed |  |  | Allow | [7 empty] | Passed: Passed ¦ Failed: Failed ¦ N/A: N/A
Standard Question | Is boot between duct and unit tight and in good condition? | Passed |  |  | Allow | [7 empty] | Passed: Passed ¦ Failed: Failed ¦ N/A: N/A
Standard Question | Is vibration isolation equipment installed & released from shipping locks? | Passed |  |  | Allow | [7 empty] | Passed: Passed ¦ Failed: Failed ¦ N/A: N/A
Standard Question | Is maintenance access acceptable for unit and components? | Passed |  |  | Allow | [7 empty] | Passed: Passed ¦ Failed: Failed ¦ N/A: N/A
Standard Question | Is sound attenuation installed? | N/A |  |  | Allow | [7 empty] | Passed: Passed ¦ Failed: Failed ¦ N/A: N/A
Standard Question | Is thermal insulation properly installed and according to specification? | Failed |  |  | Allow | [7 empty] | Passed: Passed ¦ Failed: Failed ¦ N/A: N/A
Table | Is instrumentation installed according to specification (thermometers, pressure gages, flow meters, etc.)? | Passed |  |  | Allow
Standard Question | Is clean up of equipment completed per contract documents? | Passed |  |  | Allow | [7 empty] | Passed: Passed ¦ Failed: Failed ¦ N/A: N/A
Standard Question | Are filters installed and replacement type and efficiency permanently affixed to housing--construction filters removed? | Passed |  |  | Allow | [7 empty] | Passed: Passed ¦ Failed: Failed ¦ N/A: N/A
Signature | Sign to verify successful installation: | Failed |  | Pending document submittals and thermal insulation install. | Allow |  |  |  |  | Installation Sign-off
Text Input | Notes (optional): | Passed | No additional notes. |  | Allow