## Data
NSCS Testing Database Developed by Tara Hutchinson and Xiang Wang at UCSD in 2015
Disclaimers: | This spreadsheet was prepared for the Engineering Laboratory of the National Institute of Standards and Technology (NIST) under the National Earthquake Hazards Reduction Program (NEHRP) Earthquake Structural and Engineering Research Contract SB1341-13-CQ-0009, Task Order 14-491. The contents of this publication do not necessarily reflect the views and policies of NIST or the U.S. Government.
This report was produced by the Applied Technology Council (ATC). While endeavoring to provide practical and accurate information, the Applied Technology Council, the authors, and the reviewers assume no liability for, nor express or imply any warranty with regard to, the information contained herein. Users of information contained in this report assume all liability arising from such use.
Note: | This NSCS Testing Database developed by Tara Hutchinson and Xiang Wang is referred to in the NIST report GCR 17-917-44, Seismic Analysis, Design, and Installation of Nonstructural Components and Systems – Background and Recommendations for Future Work. A downloadable copy of this report is available at https://doi.org/10.6028/NIST.GCR.17-917-44.
Test Program / Earthquake |  |  |  | General Information | [13 empty] | Frequency (experimental) [3] |  |  |  | Basis of Design | [9 empty] | Test Name | Demand (target) |  |  |  |  | Demand (measured) | [9 empty] | Demand (measured) | [8 empty] | Demand (measured) | [8 empty] | Damage State (observed) |  |  | Notes
Short Name | Ref(s) | Test Type / Instrumented | Test Facility | NSCS Type [1] | NSCS Subtype | Geometry [2] |  |  | Weight |  |  | Attachment |  |  | Mounting Condition | Location | z/h | X-Dir | Y-Dir | Z-Dir | Description | Design Standard | [11 empty] | Horizontal |  | Vertical |  | X-Direction | [9 empty] | Y-Direction | [8 empty] | Z-Direction
[6 empty] | L | W | H | Net | Design | Test | Type | Number of Attachments | Description | [8 empty] | SDS | Cp | ap | Rp | Ip | Fp,lower/Wp | Fp,upper/Wp | Fp,h/Wp | Fp,v/Wp |  | SDS | AFLX | ARID | AFLX | ARID | PGA | PFA | Sa (0.1s) | Sa (0.2s) | Sa (0.3s) | Sa (0.5s) | Sa (1.0s) | PCA | PFA/PGA | PCA/PFA | PGA | PFA | Sa (0.1s) | Sa (0.2s) | Sa (0.3s) | Sa (0.5s) | Sa (1.0s) | PCA | PFA/PGA | PGA | PFA | Sa (0.1s) | Sa (0.2s) | Sa (0.3s) | Sa (0.5s) | Sa (1.0s) | PCA | PFA/PGA
[6 empty] | (in) | (in) | (in) | (lbf) | (lbf) | (lbf) | [6 empty] | (Hz) | (Hz) | (Hz) |  |  | (g) | (unitless) | (unitless) | (unitless) | (unitless) | (unitless) | (unitless) | (unitless) | (unitless) |  | (g) | (g) | (g) | (g) | (g) | (g) | (g) | (g) | (g) | (g) | (g) | (g) | (g) | (unitless) | (unitless) | (g) | (g) | (g) | (g) | (g) | (g) | (g) | (g) | (unitless) | (g) | (g) | (g) | (g) | (g) | (g) | (g) | (g) | (unitless) | Component | Support | Anchorage
BNCS Tests | (1) - (2) | System-level, Shake Table | NEES@UCSD | Content | TV Cabinet | 35 | 21.5 | 60 | 150 | 150 | 150 | Attached to Wall w/ Nylon-adhesive Straps | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Minor | N.A. | N.A. | Limited Movement
|  |  |  | Content | Kitchen Refrigerator | 32 | 28.5 | 70 | 100 | 100 | 100 | Unattached | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Major | N.A. | N.A. | Significant Movement
|  |  |  | Content | File Cabinet | 36 | 19 | 53.5 | 180 | 180 | 180 | Unattached | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Major | N.A. | N.A. | Significant Movement
|  |  |  | Content | Lab Cabinet | 72 | 30 | 36 | 300 | 300 | 300 | Screwed into Studs | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Minor | N.A. | N.A. | Limited Movement
|  |  |  | Content | Cabinet | N.A. | N.A. | N.A. | 50 (est.) | 50 (est.) | 50 (est.) | Screwed into Studs | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Minor | N.A. | N.A. | Limited Movement
|  |  |  | Content | Table | N.A. | N.A. | N.A. | 50 (est.) | 50 (est.) | 50 (est.) | Unattached | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Major | N.A. | N.A. | Significant Movement
|  |  |  | Content | Bookcase | 24 | 12 | 60 | 70 | 70 | 70 | Unattached | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Major | N.A. | N.A. | Significant Movement
|  |  |  | Content | Deli Refrigerator | 58 | 34 | 83 | 610 | 610 | 610 | Attached to Wall w/ Ratchet Straps | N.A. | - | Floor-Mounted | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Minor | N.A. | N.A. | Limited Movement
|  |  |  | Content | Wheeled Rack | 47.25 | 18 | 60 | 65 | 65 | 65 | Unattached | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Major | N.A. | N.A. | Significant Movement
|  |  |  | Content | Freezer | 39 | 32 | 77 | 300 (est.) | 300 (est.) | 300 (est.) | Attached to Wall w/ Nylon-adhesive Straps | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Minor | N.A. | N.A. | Limited Movement
|  |  |  | Content | Cabinet | 43 | 18 | 66 | 120 | 120 | 120 | Attached to Wall-mounted Strut | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Minor | N.A. | N.A. | Limited Movement
|  |  |  | Content | Kitchen Refrigerator | 32 | 28.5 | 70 | 100 | 100 | 100 | Unattached | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Major | N.A. | N.A. | Toppled
|  |  |  | Content | Deli Refrigerator | 58 | 34 | 83 | 360 | 360 | 360 | Expansion Anchors | N.A. | - | Floor-Mounted | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Content | Freezer | 39 | 32 | 77 | 300 (est.) | 300 (est.) | 300 (est.) | Expansion Anchors | N.A. | - | Floor-Mounted | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Content | Lab Cabinet | 72 | 30 | 36 | 300 | 300 | 300 | Screwed into Studs | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Major | N.A. | N.A. | Significant Movement
|  |  |  | Content | File Cabinet | 36 | 19 | 53.5 | 100 | 100 | 100 | Unattached | N.A. | - | Free-Standing | 2nd Floor | 0.2 | - | - | - | - | Post-97 | 1.38 | - | - | - | - | - | - | - | - | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.56 | 0.84 | 1.43 | 1.79 | 1.39 | 0.69 | - | 0.875 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Major | N.A. | N.A. | Significant Movement
|  |  |  | Content | Computer server | 50 | 30 | 80 | 3000 | 3000 | 3000 | Heavy Duty Anchors | 8 | M16-25 | Floor-Mounted | 3rd Floor | 0.4 | 20 | - | - | White Noise | Post-97 | 1.38 | N.A. | 2.5 | 2.5 | 1 | 0.41 | 2.21 | 0.99 | N.A. | FB-1 | 1.38 | - | - | - | - | 0.2 | 0.32 | 0.49 | 0.72 | 0.43 | 0.3 | 1.06 | 0.33 | 1.6 | 1.0312 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Content | Computer server | 50 | 30 | 80 | 3000 | 3000 | 3000 | Heavy Duty Anchors | 8 | M16-25 | Floor-Mounted | 3rd Floor | 0.4 | 20 | - | - | White Noise | Post-97 | 1.38 | N.A. | 2.5 | 2.5 | 1 | 0.41 | 2.21 | 0.99 | N.A. | FB-2 | 1.38 | - | - | - | - | 0.18 | 0.31 | 0.46 | 0.83 | 0.42 | 0.27 | 1.18 | 0.33 | 1.7222 | 1.0645 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Content | Computer server | 50 | 30 | 80 | 3000 | 3000 | 3000 | Heavy Duty Anchors | 8 | M16-25 | Floor-Mounted | 3rd Floor | 0.4 | 20 | - | - | White Noise | Post-97 | 1.38 | N.A. | 2.5 | 2.5 | 1 | 0.41 | 2.21 | 0.99 | N.A. | FB-3 | 1.38 | - | - | - | - | 0.21 | 0.35 | 0.46 | 0.57 | 0.56 | 0.3 | 1.06 | 0.41 | 1.6667 | 1.1714 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Content | Computer server | 50 | 30 | 80 | 3000 | 3000 | 3000 | Heavy Duty Anchors | 8 | M16-25 | Floor-Mounted | 3rd Floor | 0.4 | 20 | - | - | White Noise | Post-97 | 1.38 | N.A. | 2.5 | 2.5 | 1 | 0.41 | 2.21 | 0.99 | N.A. | FB-4 | 1.38 | - | - | - | - | 0.25 | 0.37 | 0.5 | 0.48 | 0.86 | 0.48 | 1.3 | 0.55 | 1.48 | 1.4865 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Content | Computer server | 50 | 30 | 80 | 3000 | 3000 | 3000 | Heavy Duty Anchors | 8 | M16-25 | Floor-Mounted | 3rd Floor | 0.4 | 20 | - | - | White Noise | Post-97 | 1.38 | N.A. | 2.5 | 2.5 | 1 | 0.41 | 2.21 | 0.99 | N.A. | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.7 | 0.85 | 1.41 | 2.29 | 1.1 | 1.01 | 0.82 | 1.09 | 1.1714 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Content | Computer server | 30 | 50 | 80 | 3000 | 3000 | 3000 | Heavy Duty Anchors | 8 | M16-25 | Floor-Mounted | 3rd Floor | 0.4 | 5 | - | - | White Noise | Post-97 | 1.38 | N.A. | 2.5 | 2.5 | 1 | 0.41 | 2.21 | 0.99 | N.A. | FB-1 | 1.38 | - | - | - | - | 0.2 | 0.32 | 0.49 | 0.72 | 0.43 | 0.3 | 1.06 | 0.76 | 1.6 | 2.375 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Content | Computer server | 30 | 50 | 80 | 3000 | 3000 | 3000 | Heavy Duty Anchors | 8 | M16-25 | Floor-Mounted | 3rd Floor | 0.4 | 5 | - | - | White Noise | Post-97 | 1.38 | N.A. | 2.5 | 2.5 | 1 | 0.41 | 2.21 | 0.99 | N.A. | FB-2 | 1.38 | - | - | - | - | 0.18 | 0.31 | 0.46 | 0.83 | 0.42 | 0.27 | 1.18 | 0.82 | 1.7222 | 2.6452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Content | Computer server | 30 | 50 | 80 | 3000 | 3000 | 3000 | Heavy Duty Anchors | 8 | M16-25 | Floor-Mounted | 3rd Floor | 0.4 | 5 | - | - | White Noise | Post-97 | 1.38 | N.A. | 2.5 | 2.5 | 1 | 0.41 | 2.21 | 0.99 | N.A. | FB-3 | 1.38 | - | - | - | - | 0.21 | 0.35 | 0.46 | 0.57 | 0.56 | 0.3 | 1.06 | 0.72 | 1.6667 | 2.0571 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Content | Computer server | 30 | 50 | 80 | 3000 | 3000 | 3000 | Heavy Duty Anchors | 8 | M16-25 | Floor-Mounted | 3rd Floor | 0.4 | 5 | - | - | White Noise | Post-97 | 1.38 | N.A. | 2.5 | 2.5 | 1 | 0.41 | 2.21 | 0.99 | N.A. | FB-4 | 1.38 | - | - | - | - | 0.25 | 0.37 | 0.5 | 0.48 | 0.86 | 0.48 | 1.3 | 0.83 | 1.48 | 2.2432 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Content | Computer server | 30 | 50 | 80 | 3000 | 3000 | 3000 | Heavy Duty Anchors | 8 | M16-25 | Floor-Mounted | 3rd Floor | 0.4 | 5 | - | - | White Noise | Post-97 | 1.38 | N.A. | 2.5 | 2.5 | 1 | 0.41 | 2.21 | 0.99 | N.A. | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.7 | 0.85 | 1.41 | 2.29 | 1.1 | 1.01 | 2.26 | 1.09 | 3.2286 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Minor | N.A. | None | Screw withdrawal of the computer rack struts
|  |  |  | Mech. Equip. | Cooling Tower | 87.75 | 107.875 | 128 | 3500 | 6300 | 6300 | Spring Isolators | 4 | Snubber Bearing | Floor-Mounted | Roof | 1 | 5.3-5.6 | 6.5-6.7 | 4.6-4.9 | White Noise | Post-97 | 1.38 | N.A. | 2.5 | 2.5 | 1 | 0.41 | 2.21 | 1.66 | N.A. | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.99 | 1.22 | 1.58 | 2.24 | 1.36 | 2.34 | 2.32 | 1.55 | 2.3434 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Mech. Equip. | AHU | 100 | 58 | 68 | 1500 | 1500 | 1500 | Expansion Anchors | 10 | 1/2" x 3-1/4" | Floor-Mounted | Roof | 1 | - | - | - | - | Post-97 | 1.38 | N.A. | 2.5 | 6 | 1 | 0.41 | 2.21 | 0.69 | N.A. | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.99 | 1.22 | 1.58 | 2.24 | 1.36 | 2.34 | 0.97 | 1.55 | 0.9798 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | N.A. | None | No observed damage
|  |  |  | Architectural | Penthouse | 240 | 120 | 120 | 3500 | 3500 | 3500 | Expansion Anchors | 30 | 1/2" x 3-1/4" @ 24" o.c. | Floor-Mounted | Roof | 1 | 15 (est.) | >20 (est.) | - | White Noise | Post-97 | 1.38 | N.A. | 1 | 3.5 | 1 | 0.41 | 2.21 | 1.18 | N.A. | FB-5 | 1.38 | - | - | - | - | 0.64 | 0.99 | 1.22 | 1.58 | 2.24 | 1.36 | 2.34 | 1.1 | 1.55 | 1.1111 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Minor | N.A. | None | Incipient screw pullout and joint tape cracking
UB Qual. Tests | (3) | Component-level, Shake Table | UB-SEESL | Mech. Equip. | Cooling Tower | 87.25 | 107.125 | 137.875 | 4050 | - | 6810 | Spring Isolators | 4 | Isolator-Type I | Floor-Mounted | N.A. | N.A. | 1.13 | 1.38 | 3.69 | White Noise | Post-97 | - | - | 2.5 | 2.5 | 1 | - | - | 0.2 | 0.15 | Level-1 | - | 0.5 | 0.37 | 0.33 | 0.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | No observed damage
|  |  |  | Mech. Equip. | Cooling Tower | 87.25 | 107.125 | 137.875 | 4050 | - | 6810 | Spring Isolators | 4 | Isolator-Type II | Floor-Mounted | N.A. | N.A. | - | - | - | - | Post-97 | - | - | 2.5 | 2.5 | 1 | - | - | 0.4 | 0.3 | Level-2 | - | 1 | 0.75 | 0.67 | 0.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | No observed damage
|  |  |  | Mech. Equip. | Cooling Tower | 87.25 | 107.125 | 137.875 | 4050 | - | 6810 | Spring Isolators | 4 | Isolator-Type II | Floor-Mounted | N.A. | N.A. | - | - | - | - | Post-97 | - | - | 2.5 | 2.5 | 1 | - | - | 0.8 | 0.6 | Level-3 | - | 2 | 1.5 | 1.33 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | No observed damage
|  |  |  | Mech. Equip. | Cooling Tower | 87.25 | 107.125 | 137.875 | 4050 | - | 6810 | Spring Isolators | 4 | Isolator-Type II | Floor-Mounted | N.A. | N.A. | - | - | - | - | Post-97 | - | - | 2.5 | 2.5 | 1 | - | - | 1 | 0.75 | Level-4 | - | 2.5 | 1.88 | 1.67 | 1.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | No observed damage
|  |  |  | Mech. Equip. | Cooling Tower | 87.25 | 107.125 | 137.875 | 4050 | - | 6810 | Spring Isolators | 4 | Isolator-Type II | Floor-Mounted | N.A. | N.A. | 1.03 | 1.25 | 2.38 | White Noise | Post-97 | - | - | 2.5 | 2.5 | 1 | - | - | 0.2 | 0.15 | Level-1 | - | 0.5 | 0.37 | 0.33 | 0.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | No observed damage
|  |  |  | Mech. Equip. | Cooling Tower | 87.25 | 107.125 | 137.875 | 4050 | - | 6810 | Spring Isolators | 4 | Isolator-Type II | Floor-Mounted | N.A. | N.A. | - | - | - | - | Post-97 | - | - | 2.5 | 2.5 | 1 | - | - | 1 | 0.75 | Level-4 | - | 2.5 | 1.88 | 1.67 | 1.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | No observed damage
|  |  |  | Mech. Equip. | Cooling Tower | 87.25 | 107.125 | 137.875 | 4050 | - | 6810 | Spring Isolators | 4 | Isolator-Type II | Floor-Mounted | N.A. | N.A. | - | - | - | - | Post-97 | - | - | 2.5 | 2.5 | 1 | - | - | 1.2 | 0.9 | Level-5 | - | 3 | 2.25 | 2 | 1.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | No observed damage
SEAONC Tests | (4) | Component-level, Shake Table | UC-Berkeley | Content | Refrigerator | 34 | 38.5 | 75 | 900 | 900 | 900 | Angles with Expansion Anchors | 6 | (2) L8x3x1/8x1'-10", (12) #12 SMS, (6) 3/8"x 2" embed Hilti KBTZs | Floor-Mounted | Mid height | 0.5 | - | - | - | - | CBC-2013 | 1.13 | - | 1 | 2.5 | 1.5 | 0.51 | 2.72 | 0.54 | 0.23 | - | 1.62 | 2.59 | 1.3 | 0 | 0 | - | 0.48 | 0.47854 | 0.69587 | 0.63794 | 1.1836 | 0.22886 | 0.77 | - | 1.6042 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | 1D shaking - Motion perpendicular to the long side of the angle; No vertical component; "225-year" UCSF Parnassus HSIR; filtered PFA and PCA
|  |  |  | Content | Refrigerator | 34 | 38.5 | 75 | 900 | 900 | 900 | Angles with Expansion Anchors | 6 | (2) L8x3x1/8x1'-10", (12) #12 SMS, (6) 3/8"x 2" embed Hilti KBTZs | Floor-Mounted | Mid height | 0.5 | - | - | - | - | CBC-2013 | 1.13 | - | 1 | 2.5 | 1.5 | 0.51 | 2.72 | 0.54 | 0.23 | - | 1.62 | 2.59 | 1.3 | 0 | 0 | - | 0.53 | 0.7123 | 1.0369 | 0.76798 | 1.4128 | 0.43225 | 1.2 | - | 2.2642 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | 1D shaking - Motion perpendicular to the long side of the angle; No vertical component; "475-year" UCSF Parnassus HSIR; filtered PFA and PCA
|  |  |  | Content | Refrigerator | 34 | 38.5 | 75 | 900 | 900 | 900 | Angles with Expansion Anchors | 6 | (2) L8x3x1/8x1'-10", (12) #12 SMS, (6) 3/8"x 2" embed Hilti KBTZs | Floor-Mounted | Mid height | 0.5 | - | - | - | - | CBC-2013 | 1.13 | - | 1 | 2.5 | 1.5 | 0.51 | 2.72 | 0.54 | 0.23 | - | 1.62 | 2.59 | 1.3 | 0 | 0 | - | 0.64 | 0.82523 | 0.92528 | 1.04 | 1.6597 | 0.59304 | 1.41 | - | 2.2031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | 1D shaking - Motion perpendicular to the long side of the angle; No vertical component; "975-year" UCSF Parnassus HSIR; filtered PFA and PCA
|  |  |  | Content | Refrigerator | 34 | 38.5 | 75 | 900 | 900 | 900 | Angles with Expansion Anchors | 6 | (2) L8x3x1/8x1'-10", (12) #12 SMS, (6) 3/8"x 2" embed Hilti KBTZs | Floor-Mounted | Mid height | 0.5 | - | - | - | - | CBC-2013 | 1.13 | - | 1 | 2.5 | 1.5 | 0.51 | 2.72 | 0.54 | 0.23 | - | 1.62 | 2.59 | 1.3 | 0 | 0 | - | 0.75 | 1.1305 | 1.0521 | 0.98724 | 1.6707 | 0.49166 | 1.75 | - | 2.3333 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | 1D shaking - Motion perpendicular to the long side of the angle; No vertical component; "2475-year" UCSF Parnassus HSIR; filtered PFA and PCA
|  |  |  | Content | Refrigerator | 34 | 38.5 | 75 | 900 | 900 | 900 | Angles with Expansion Anchors | 6 | (2) L8x3x1/8x1'-10", (12) #12 SMS, (6) 3/8"x 2" embed Hilti KBTZs | Floor-Mounted | Mid height | 0.5 | - | - | - | - | CBC-2013 | 1.13 | - | 1 | 2.5 | 1.5 | 0.51 | 2.72 | 0.54 | 0.23 | - | 1.62 | 2.59 | 1.3 | 0 | 0 | - | 1.15 | 2.3984 | 2.5855 | 2.5759 | 2.606 | 1.9739 | 2.87 | - | 2.4957 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | 1D shaking - Motion perpendicular to the long side of the angle; No vertical component; "975-year spectral match" UCSF Parnassus HSIR; filtered PFA and PCA
|  |  |  | Content | Refrigerator | 34 | 38.5 | 75 | 900 | 900 | 900 | Angles with Expansion Anchors | 6 | (2) L8x3x1/8x1'-10", (12) #12 SMS, (6) 3/8"x 2" embed Hilti KBTZs | Floor-Mounted | Mid height | 0.5 | - | - | - | - | CBC-2013 | 1.13 | - | 1 | 2.5 | 1.5 | 0.51 | 2.72 | 0.54 | 0.23 | - | 1.62 | 2.59 | 1.3 | 0 | 0 | - | 0.5 | 0.47854 | 0.69587 | 0.63794 | 1.1836 | 0.22886 | 0.98 | - | 1.96 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | 1D shaking - Motion parallel to the long side of the angle; No vertical component; "225-year" UCSF Parnassus HSIR; filtered PFA and PCA
|  |  |  | Content | Refrigerator | 34 | 38.5 | 75 | 900 | 900 | 900 | Angles with Expansion Anchors | 6 | (2) L8x3x1/8x1'-10", (12) #12 SMS, (6) 3/8"x 2" embed Hilti KBTZs | Floor-Mounted | Mid height | 0.5 | - | - | - | - | CBC-2013 | 1.13 | - | 1 | 2.5 | 1.5 | 0.51 | 2.72 | 0.54 | 0.23 | - | 1.62 | 2.59 | 1.3 | 0 | 0 | - | 0.55 | 0.7123 | 1.0369 | 0.76798 | 1.4128 | 0.43225 | 1.32 | - | 2.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | 1D shaking - Motion parallel to the long side of the angle; No vertical component; "475-year" UCSF Parnassus HSIR; filtered PFA and PCA
|  |  |  | Content | Refrigerator | 34 | 38.5 | 75 | 900 | 900 | 900 | Angles with Expansion Anchors | 6 | (2) L8x3x1/8x1'-10", (12) #12 SMS, (6) 3/8"x 2" embed Hilti KBTZs | Floor-Mounted | Mid height | 0.5 | - | - | - | - | CBC-2013 | 1.13 | - | 1 | 2.5 | 1.5 | 0.51 | 2.72 | 0.54 | 0.23 | - | 1.62 | 2.59 | 1.3 | 0 | 0 | - | 0.72 | 0.82523 | 0.92528 | 1.04 | 1.6597 | 0.59304 | 1.29 | - | 1.7917 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | 1D shaking - Motion parallel to the long side of the angle; No vertical component; "975-year" UCSF Parnassus HSIR; filtered PFA and PCA
|  |  |  | Content | Refrigerator | 34 | 38.5 | 75 | 900 | 900 | 900 | Angles with Expansion Anchors | 6 | (2) L8x3x1/8x1'-10", (12) #12 SMS, (6) 3/8"x 2" embed Hilti KBTZs | Floor-Mounted | Mid height | 0.5 | - | - | - | - | CBC-2013 | 1.13 | - | 1 | 2.5 | 1.5 | 0.51 | 2.72 | 0.54 | 0.23 | - | 1.62 | 2.59 | 1.3 | 0 | 0 | - | 0.77 | 1.1305 | 1.0521 | 0.98724 | 1.6707 | 0.49166 | 1.46 | - | 1.8961 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | 1D shaking - Motion parallel to the long side of the angle; No vertical component; "2475-year" UCSF Parnassus HSIR; filtered PFA and PCA
|  |  |  | Content | Refrigerator | 34 | 38.5 | 75 | 900 | 900 | 900 | Angles with Expansion Anchors | 6 | (2) L8x3x1/8x1'-10", (12) #12 SMS, (6) 3/8"x 2" embed Hilti KBTZs | Floor-Mounted | Mid height | 0.5 | - | - | - | - | CBC-2013 | 1.13 | - | 1 | 2.5 | 1.5 | 0.51 | 2.72 | 0.54 | 0.23 | - | 1.62 | 2.59 | 1.3 | 0 | 0 | - | 1.17 | 2.3984 | 2.5855 | 2.5759 | 2.606 | 1.9739 | 2.49 | - | 2.1282 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | Minor | 1D shaking - Motion parallel to the long side of the angle; No vertical component; "975-year spectral match" UCSF Parnassus HSIR; filtered PFA and PCA
ERDC-CERL Tests | (5) | Component-level, Shake Table | ERDC-CERL | Mech. Equip. | Cooling Tower | 215.75 | 142 | 211.125 | 15140 | 23630 | 22173 | Spring Isolators | 8 | Mason Industries SLFADA350-SLF-109 | Floor-Mounted | Roof | 1 | 2 | 1.8 | 3.8 | Uniaxial Sine-sweep Tests | CBC-2013 | 1.3 | - | - | - | - | - | - | - | - | - | 1.3 | 2.08 | 1.56 | 1.391 | 0.559 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0001-10 -- PT2-1218A-3S1/S -- Baltimore Aircoil
|  |  |  | Mech. Equip. | Cooling Tower | 215.75 | 142 | 211.125 | 15140 | 23630 | 22173 | Rigid | 8 | 3/4" dia Grade 5 bolts | Floor-Mounted | Roof | 1 | 6.3 | 3.5 | 8.5 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 2.4 | 2.14 | 0.86 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0001-10 -- PT2-1218A-3S1/S -- Baltimore Aircoil
|  |  |  | Mech. Equip. | Cooling Tower | 215.75 | 142 | 211.125 | 15140 | 23630 | 22173 | Spring Isolators | 8 | Mason Industries SLFADA350-SLF-109 | Floor-Mounted | Roof | 1 | 2 | 1.8 | 3.8 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 2.4 | 1.34 | 0.54 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0001-10 -- PT2-1218A-3S1/S -- Baltimore Aircoil
|  |  |  | Mech. Equip. | Hermetic Centrifugal Chillers | 169.25 | 73.0625 | 75.25 | - | 15209 | 15209 | Rigid | N.A. | Unit legs welded to adapter plates | Floor-Mounted | Roof | 1 | 19 | 20 | 25 | Uniaxial Sine-sweep Tests | CBC-2013 | 2.1 | - | - | - | - | - | - | - | - | - | 2.1 | 3.36 | 2.52 | 1.4 | 0.56 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0026-10 -- Frame 2, 19XRV-2222287BHH64 -- Carrier
|  |  |  | Mech. Equip. | Hermetic Centrifugal Chillers | 262.5 | 125 | 119.25 | - | 60401 | 60401 | Rigid | 24 | 3/4" dia Grade 8 bolts | Floor-Mounted | Roof | 1 | 6.1 | 8.5 | 15 | Uniaxial Sine-sweep Tests | CBC-2013 | 2.1 | - | - | - | - | - | - | - | - | - | 2.1 | 3.36 | 2.52 | 1.4 | 0.56 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0026-10 -- Frame 8, 19XRV8Z8955DMBH64 -- Carrier
|  |  |  | Mech. Equip. | Hermetic Centrifugal Chillers | 262.5 | 125 | 119.25 | - | 68839 | 68839 | Rigid | 24 | 3/4" dia Grade 8 bolts | Floor-Mounted | Roof | 1 | 8.1 | 11.7 | 21.8 | Uniaxial Sine-sweep Tests | CBC-2013 | 2.1 | - | - | - | - | - | - | - | - | - | 2.1 | 3.36 | 2.52 | 1.4 | 0.56 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0026-10 -- Frame 8, 19XR-8989E61EPCD68 -- Carrier
|  |  |  | Mech. Equip. | Hermetic Centrifugal Chillers | 264.5 | 79 | 132.18 | - | 77334 | 77334 | Rigid | 24 | 11/4" dia Grade 8 bolts | Floor-Mounted | Roof | 1 | 7 | 11 | 17 | Uniaxial Sine-sweep Tests | CBC-2013 | 1.64 | - | - | - | - | - | - | - | - | - | 1.64 | 2.64 | 1.97 | 1.09 | 0.44 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0026-10 -- Frame C-D, 19XR-C67D67736ZZG -- Carrier
|  |  |  | Mech. Equip. | Hermetic Centrifugal Chillers | 264.5 | 77.5 | 150.3 | - | 78558 | 78558 | Rigid | 24 | 11/4" dia Grade 8 bolts | Floor-Mounted | Roof | 1 | 9 | 12 | 22 | Uniaxial Sine-sweep Tests | CBC-2013 | 1.64 | - | - | - | - | - | - | - | - | - | 1.64 | 2.64 | 1.97 | 1.09 | 0.44 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0026-10 -- Frame C-D, 19XR-C67D67736ZZG -- Carrier
|  |  |  | Mech. Equip. | Flooded Chiller | 181 | 73.625 | 120.125 | - | 26285 | 26275 | Rigid | 8 | 7/8" dia Grade 8 bolts | Floor-Mounted | Roof | 1 | 11.3 | 9.4 | 28 | Uniaxial Sine-sweep Tests | CBC-2013 | 1.93 | - | - | - | - | - | - | - | - | - | 1.93 | 3.09 | 2.32 | 1.29 | 0.51 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0204-10 -- MS_F MagLev MS0600FC1L -- Multistack
|  |  |  | Mech. Equip. | Flooded Chiller | 168.8125 | 42.5 | 94.375 | - | 15350 | 15350 | Rigid | 8 | 7/8" dia Grade 8 bolts | Floor-Mounted | Roof | 1 | 6.5 | 5.5 | 11.8 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 2.4 | 1.33 | 0.53 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0204-10 -- MS_F MagLev MS0482FC1L -- Multistack
|  |  |  | Mech. Equip. | Generator Sets | 75.9843 | 37.4016 | 45.1575 | - | 1850 | 1850 | Rigid | 8 | 5/8" dia Grade 8 bolts | Floor-Mounted | Roof | 0.68 | 10 | 6.6 | 17 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 1.88 | 1.34 | 0.54 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0282-10 -- 35 kW diesel generator alone -- Generac
|  |  |  | Mech. Equip. | Generator Sets | 112.4803 | 37.9921 | 62.3622 | - | 2900 | 2900 | Rigid | 8 | 5/8" dia Grade 8 bolts | Floor-Mounted | Roof | 0.68 | 9.1 | 6.5 | 16 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 1.88 | 1.34 | 0.54 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0282-10 -- 35 kW w/enclosure & empty fuel tank -- Generac
|  |  |  | Mech. Equip. | Generator Sets | 112.4803 | 37.9921 | 62.3622 | - | 3350 | 3350 | Rigid | 8 | 5/8" dia Grade 8 bolts | Floor-Mounted | Roof | 0.68 | 8.7 | 6.3 | 16 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 1.88 | 1.34 | 0.54 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0282-10 -- 35 kW w/enclosure & full fuel tank -- Generac
|  |  |  | Mech. Equip. | Generator Sets | 136.0236 | 57.5984 | 67.8346 | - | 6400 | 6400 | Rigid | 10 | 5/8" dia Grade 8 bolts | Floor-Mounted | Roof | 0.68 | 8.1 | 5.6 | 14 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 1.88 | 1.34 | 0.54 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0282-10 -- 350 kW diesel generator alone -- Generac
|  |  |  | Mech. Equip. | Generator Sets | 277.7559 | 57.5984 | 146.6929 | - | 13450 | 13450 | Rigid | 16 | 3/4" dia Grade 8 bolts | Floor-Mounted | Roof | 0.68 | 5.4 | 4.1 | 12 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 1.88 | 1.34 | 0.54 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0282-10 -- 350 kW w/enclosure & empty fuel tank -- Generac
|  |  |  | Mech. Equip. | Generator Sets | 277.7559 | 57.5984 | 146.6929 | - | 24700 | 24700 | Rigid | 16 | 3/4" dia Grade 8 bolts | Floor-Mounted | Roof | 0.68 | 4.9 | 4.1 | 12 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 1.88 | 1.34 | 0.54 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0282-10 -- 350 kW w/enclosure & full fuel tank -- Generac
|  |  |  | Mech. Equip. | Uninterruptable Power Supply | 140.5 | 39.4 | 76.8 | 13800 | 13800 | 13800 | Rigid | 22 | 3/4" dia bolts and angle brackets | Floor-Mounted | Mid-floor | 0.57 | 7.5 | 5 | 18 | Uniaxial Sine-sweep Tests | - | 2.1 | - | - | - | - | - | - | - | - | - | 2.1 | 3.36 | 1.8 | 1.4 | 0.56 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0285-10 -- 750kVA UPS -- Emerson Network Power
|  |  |  | Mech. Equip. | Uninterruptable Power Supply | 228.3 | 47.2 | 78.7 | 21450 | 21450 | 21450 | Rigid | 30 | 3/4" dia bolts and angle brackets | Floor-Mounted | Mid-floor | 0.57 | 8 | 5.7 | 14 | Uniaxial Sine-sweep Tests | - | 2.1 | - | - | - | - | - | - | - | - | - | 2.1 | 3.36 | 1.9 | 1.4 | 0.56 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0285-10 -- 1100kVA UPS -- Emerson Network Power
|  |  |  | Mech. Equip. | Bypass Cabinet | 25.6 | 33.5 | 76.8 | 755 | 755 | 755 | Rigid | 4 | 3/4" dia bolts and angle brackets | Floor-Mounted | Mid-floor | 0.61 | 7.9 | 20 | - | Uniaxial Sine-sweep Tests | - | 2.5 | - | - | - | - | - | - | - | - | - | 2.5 | 4 | 2.22 | 1.67 | 0.67 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0285-10 -- 250kVA maintenance by-pass cabinet -- Emerson Network Power
|  |  |  | Mech. Equip. | Bypass Cabinet | 25.6 | 39.4 | 76.8 | 755 | 755 | 755 | Rigid | 4 | 3/4" dia bolts and angle brackets | Floor-Mounted | Mid-floor | 0.61 | 9 | 20 | - | Uniaxial Sine-sweep Tests | - | 2.5 | - | - | - | - | - | - | - | - | - | 2.5 | 4 | 2.22 | 1.67 | 0.67 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0285-10 -- 500kVA maintenance by-pass cabinet -- Emerson Network Power
|  |  |  | Mech. Equip. | Junction Cabinet | 15.5 | 33.5 | 76.8 | 255 | 255 | 255 | Rigid | - | 3/4" dia bolts and angle brackets | Floor-Mounted | Mid-floor | 0.55 | 11 | 8 | - | Uniaxial Sine-sweep Tests | - | 2.15 | - | - | - | - | - | - | - | - | - | 2.15 | 3.44 | 1.81 | 1.43 | 0.57 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0285-10 -- 12V narrow junction cabinet -- Emerson Network Power
|  |  |  | Mech. Equip. | Junction Cabinet | 17.5 | 33.5 | 76.8 | 255 | 255 | 255 | Rigid | - | 3/4" dia bolts and angle brackets | Floor-Mounted | Mid-floor | 0.57 | 5.4 | 7.3 | 25 | Uniaxial Sine-sweep Tests | - | 2.05 | - | - | - | - | - | - | - | - | - | 2.05 | 3.28 | 1.75 | 1.37 | 0.55 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0285-10 -- 16V narrow junction cabinet -- Emerson Network Power
|  |  |  | Mech. Equip. | Battery Cabinet | 56.1 | 33.5 | 76.8 | 5500 | 5500 | 4650 | Rigid | - | 3/4" dia bolts and angle brackets | Floor-Mounted | Mid-floor | 0.55 | 11 | 8.6 | 23 | Uniaxial Sine-sweep Tests | - | 2.15 | - | - | - | - | - | - | - | - | - | 2.15 | 3.44 | 1.81 | 1.43 | 0.57 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0285-10 -- 12V top terminal battery cabinet -- Emerson Network Power
|  |  |  | Mech. Equip. | Battery Cabinet | 63 | 33.5 | 76.8 | 8990 | 8990 | 8650 | Rigid | - | 3/4" dia bolts and angle brackets | Floor-Mounted | Mid-floor | 0.57 | 5.4 | 7.2 | 25 | Uniaxial Sine-sweep Tests | - | 2.05 | - | - | - | - | - | - | - | - | - | 2.05 | 3.28 | 1.75 | 1.37 | 0.55 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0285-10 -- 16V front terminal battery cabinet -- Emerson Network Power
|  |  |  | Mech. Equip. | Air-cooled Screw Liquid Chiller | 252 | 93 | 96 | - | 13801 | - | Captive Mount Isolators | 10 | VMC YRSM3 2300Z, 1300Z & 1000Z | Floor-Mounted | Roof | 1 | 6.9 | 4.7 | 9 | Uniaxial Sine-sweep Tests | CBC-2013 | 1.95 | - | - | - | - | - | - | - | - | - | 1.95 | 3.12 | 2.34 | 1.3 | 0.52 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0317-10 -- YVAA0165/QTC4165T -- Johnson Controls
|  |  |  | Mech. Equip. | Air-cooled Screw Liquid Chiller | 428.1 | 93 | 96 | - | 22193 | - | Captive Mount Isolators | 12 | VMC YRSM3 2300Z & 1000Z | Floor-Mounted | Roof | 1 | 7 | 3.6 | 8 | Uniaxial Sine-sweep Tests | CBC-2013 | 1.95 | - | - | - | - | - | - | - | - | - | 1.95 | 3.12 | 2.34 | 1.3 | 0.52 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0317-10 -- YVAA0343 -- Johnson Controls
|  |  |  | Mech. Equip. | Diesel Generator Set | 286 | 81 | 124 | - | 32000 | 32000 | Rigid | 18 | M16 ISO 10.9 Grade bolts with nuts | Floor-Mounted | Ground | 0 | 6.2 | 4.8 | 10.5 | Uniaxial Sine-sweep Tests | CBC-2013 | 2.26 | - | - | - | - | - | - | - | - | - | 2.26 | 2.26 | 0.9 | 1.51 | 0.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0321-10 -- C18 (600kW) w/enclosure & full tank -- Caterpillar Electric Power
|  |  |  | Mech. Equip. | Air Conditioner | 533 | 139 | 104 | - | 17655 | 17655 | Rigid | - | #14 SMS @ 6" o.c., along the length | Floor-Mounted | Roof | 1 | 6.6 | 5.7 | 21.1 | Uniaxial Sine-sweep Tests | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0323-10 -- InteliPak II, SLHJ090 (90 ton) -- Trane
|  |  |  | Mech. Equip. | Cooling Tower | 107.75 | 94.25 | 100.75 | 3875 | 7485 | 7000 | Rigid | 6 | 3/4" dia Grade 5 bolts | Floor-Mounted | Roof | 1 | 11.2 | 12.2 | >33 | Uniaxial Sine-sweep Tests | CBC-2013 | 2.1 | - | - | - | - | - | - | - | - | - | 2.1 | 3.36 | 2.52 | 1.41 | 0.57 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0384-10 -- XES15E-0809-06DE -- Baltimore Aircoil
|  |  |  | Mech. Equip. | Cooling Tower | 107.75 | 94.25 | 100.75 | 3875 | 7485 | 7000 | Spring Isolators | 4 | Mason Industries SLFADA350-SLF-107 | Floor-Mounted | Roof | 1 | 3 | 3 | 5 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 2.4 | 1.34 | 0.54 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0384-10 -- XES15E-0809-06DE -- Baltimore Aircoil
|  |  |  | Mech. Equip. | Cooling Tower | 107.75 | 94.25 | 100.75 | 3875 | 7485 | 7000 | Spring Isolators | 4 | Mason Industries SLFADA350-SLF-107 | Floor-Mounted | Roof | 1 | 2.5 | 3 | 4.8 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 2.4 | 1.34 | 0.54 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0384-10 -- XES15E-0809-06DE -- Baltimore Aircoil
|  |  |  | Mech. Equip. | Cooling Tower | 107.75 | 94.25 | 100.75 | 3875 | 7485 | 7000 | Rigid | 6 | 3/4" dia Grade 5 bolts | Floor-Mounted | Roof | 1 | 10.5 | 12 | >33 | Uniaxial Sine-sweep Tests | CBC-2013 | 2.1 | - | - | - | - | - | - | - | - | - | 2.1 | 3.36 | 2.52 | 1.41 | 0.57 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0384-10 -- XES15E-0809-06DE -- Baltimore Aircoil
|  |  |  | Mech. Equip. | Cooling Tower | 215.75 | 142 | 207 | 15184 | 31844 | 25600 | Rigid | 12 | 3/4" dia Grade 5 bolts | Floor-Mounted | Roof | 1 | 4 | 4.5 | 22.2 | Uniaxial Sine-sweep Tests | CBC-2013 | 2.1 | - | - | - | - | - | - | - | - | - | 2.1 | 3.36 | 2.52 | 1.41 | 0.57 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0384-10 -- S15E-1218-12MN -- Baltimore Aircoil
|  |  |  | Mech. Equip. | Cooling Tower | 215.75 | 142 | 207 | 15184 | 31844 | 25600 | Spring Isolators | 4 | Mason Industries SLFADA350-SLF-109 | Floor-Mounted | Roof | 1 | 1.25 | 1.25 | 3.5 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 2.4 | 1.34 | 0.54 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0384-10 -- S15E-1218-12MN -- Baltimore Aircoil
|  |  |  | Mech. Equip. | Cooling Tower | 215.75 | 142 | 207 | 15184 | 31844 | 25600 | Spring Isolators | 2 | Mason Industries SLFADA350-SLF-111 | Floor-Mounted | Roof | 1 | 1.25 | 1.25 | 3.5 | Uniaxial Sine-sweep Tests | CBC-2013 | 2 | - | - | - | - | - | - | - | - | - | 2 | 3.2 | 2.4 | 1.34 | 0.54 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | None | None | None | OSP-0384-10 -- S15E-1218-12MN -- Baltimore Aircoil
Northridge EQ | (6) | Instrumented |  | Electrical Equip. | Transformer | 84 | 54 | 91.5 | 9130 | 9130 | N.A. | Expansion Anchors | 12 | 6 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | IXFMR ·Sub. A, Sect. 1
|  |  |  | Electrical Equip. | Transformer | 84 | 54 | 91.5 | 9130 | 9130 | N.A. | Expansion Anchors | 12 | 6 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | IXFMR ·Sub. A, Sect. 2
|  |  |  | Electrical Equip. | Transformer | 84 | 54 | 91.5 | 9130 | 9130 | N.A. | Expansion Anchors | 12 | 6 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | IXFMR ·Sub. B, Sect. 1
|  |  |  | Electrical Equip. | Transformer | 84 | 54 | 91.5 | 9130 | 9130 | N.A. | Expansion Anchors | 12 | 6 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | IXFMR ·Sub. B, Sect. 2
|  |  |  | Electrical Equip. | Transformer | 84 | 66 | 91.5 | 6700 | 6700 | N.A. | Expansion Anchors | 12 | 6 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SWGR - Sub. A, Sect. 1
|  |  |  | Electrical Equip. | Transformer | 93 | 66 | 91.5 | 4950 | 4950 | N.A. | Expansion Anchors | 12 | 6 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SWGR - Sub. A, Sect. 2
|  |  |  | Electrical Equip. | Transformer | 147 | 66 | 91.5 | 12000 | 12000 | N.A. | Expansion Anchors | 12 | 6 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SWGR - Sub. B
|  |  |  | Electrical Equip. | Transformer | 34 | 54 | 91.5 | 1300 | 1300 | N.A. | Expansion Anchors | 8 | 4 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | High Voltage · Sub. A, Sect. 1
|  |  |  | Electrical Equip. | Transformer | 34 | 54 | 91.5 | 1300 | 1300 | N.A. | Expansion Anchors | 8 | 4 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | High Voltage · Sub. A, Sect. 2
|  |  |  | Electrical Equip. | Transformer | 34 | 54 | 91.5 | 1300 | 1300 | N.A. | Expansion Anchors | 8 | 4 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | High Voltage · Sub. A. Sect. 1
|  |  |  | Electrical Equip. | Transformer | 34 | 54 | 91.5 | 1300 | 1300 | N.A. | Expansion Anchors | 8 | 4 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | High Voltage · Sub. A, Sect. 2
|  |  |  | Electrical Equip. | Auto Transfer Switch | 32 | 32 | 107.5 | 1350 | 1350 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | IATS (typ. of two)
|  |  |  | Electrical Equip. | Auto Transfer Switch | 32 | 32 | 107.5 | 1350 | 1350 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | IATS (typ. of four)
|  |  |  | Electrical Equip. | Transformer | 28 | 15 | 37 | 690 | 690 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | IXFMR - 75 KVA (two)
|  |  |  | Electrical Equip. | Transformer | 45 | 28 | 48 | 2500 | 2500 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 300 KVA
|  |  |  | Electrical Equip. | Transformer | 45 | 28 | 48 | 2500 | 2500 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 300 KVA
|  |  |  | Electrical Equip. | Transformer | 33 | 22 | 42 | 1050 | 1050 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 112.5 KVA
|  |  |  | Electrical Equip. | Transformer | 45 | 28 | 48 | 2500 | 2500 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 300 KVA
|  |  |  | Electrical Equip. | Transformer | 45 | 28 | 48 | 2000 | 2000 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 225 KVA
|  |  |  | Electrical Equip. | Transformer | 28 | 15 | 30 | 590 | 590 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 45 KVA
|  |  |  | Electrical Equip. | Transformer | 45 | 28 | 48 | 2500 | 2500 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | 2nd Floor | 0.2 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.49 (est.) | - | - | - | - | - | - | 1.2895 | - | 0.8 | 0.9 (est.) | - | - | - | - | - | - | 1.125 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 300 KVA
|  |  |  | Electrical Equip. | Transformer | 33 | 22 | 42 | 1050 | 1050 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | 2nd Floor | 0.2 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.49 (est.) | - | - | - | - | - | - | 1.2895 | - | 0.8 | 0.9 (est.) | - | - | - | - | - | - | 1.125 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 112.5 KVA
|  |  |  | Electrical Equip. | Transformer | 45 | 28 | 48 | 2000 | 2000 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 225 KVA
|  |  |  | Electrical Equip. | Transformer | 28 | 15 | 30 | 590 | 590 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 45 KVA
|  |  |  | Electrical Equip. | Transformer | 33 | 22 | 42 | 1050 | 1050 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 112.5 KVA
|  |  |  | Electrical Equip. | Transformer | 45 | 28 | 48 | 2500 | 2500 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 300 KVA
|  |  |  | Electrical Equip. | Transformer | 33 | 22 | 42 | 1050 | 1050 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 112.5 KVA
|  |  |  | Electrical Equip. | Transformer | 45 | 28 | 48 | 2500 | 2500 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | XFMR - 300 KVA
|  |  |  | Electrical Equip. | Transformer | 45 | 28 | 48 | 2000 | 2000 | N.A. | Expansion Anchors | 3 | 3 - 5/8" exp. anchor | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | Major | XFMR - 225 KVA. Anchor failure, unit displaced.
|  |  |  | Electrical Equip. | Switchgear | 48 | 14 | 90 | 708 | 708 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DHN1A
|  |  |  | Electrical Equip. | Switchgear | 48 | 14 | 90 | 1474 | 1474 | N.A. | Expansion Anchors | 4 | 4 - 1/2" anchors | Floor-Mounted | 2nd Floor | 0.2 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.49 (est.) | - | - | - | - | - | - | 1.2895 | - | 0.8 | 0.9 (est.) | - | - | - | - | - | - | 1.125 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DHN1B
|  |  |  | Electrical Equip. | Switchgear | 48 | 14 | 90 | 740 | 740 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DHN1C - 11 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 48 | 14 | 90 | 690 | 690 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DHN2D - 11 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 42 | 14 | 90 | 593 | 593 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DHN1F - 11 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 84 | 24 | 90.5 | 1523 | 1523 | N.A. | Expansion Anchors | 4 | 4 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DHN1H - 21 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 42 | 14 | 90 | 694 | 694 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DHN1J - 11 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 42 | 14 | 90 | 556 | 556 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DLN1A - 11 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 42 | 14 | 90 | 602 | 602 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DLN1B - 11 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 42 | 14 | 90 | 574 | 574 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DLN1C - 11 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 42 | 14 | 90 | 575 | 575 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | 2nd Floor | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.49 (est.) | - | - | - | - | - | - | 1.2895 | - | 0.8 | 0.9 (est.) | - | - | - | - | - | - | 1.125 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DLN2D - 11 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 42 | 14 | 90 | 1250 | 1250 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DLN1H - 11 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 42 | 14 | 90 | 1250 | 1250 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | DLN1J - 11 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 48 | 24 | 91.5 | 1000 | 1000 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | EL-1 - 21 Straps at top
|  |  |  | Electrical Equip. | Switchgear | 48 | 24 | 91.5 | 1000 | 1000 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | EC-1 - 21 Straps at top
|  |  |  | Electrical Equip. | MCC | 100 | 20 | 91.62 | 3790 | 3790 | N.A. | Expansion Anchors | 4 | 4 - 1/2" anchors | Floor-Mounted/Wall Supported | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | Minor | None | MCC·EA- 4 straps at top welded to steel shear wall. Some failed, base of units slid.
|  |  |  | Electrical Equip. | MCC | 100 | 20 | 91.62 | 3790 | 3790 | N.A. | Expansion Anchors | 4 | 4 - 1/2" anchors | Floor-Mounted/Wall Supported | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | Minor | None | MCC·EB. Sec. 1 - 4 straps at top welded to steel shear wall. Some failed, base of units slid.
|  |  |  | Electrical Equip. | MCC | 40 | 20 | 91.62 | 1420 | 1420 | N.A. | Expansion Anchors | 4 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | Minor | None | MCC·EB. Sec. 2 - 2 straps at top welded to steel shear wall. Some failed, base of units slid.
|  |  |  | Electrical Equip. | MCC | 160 | 20 | 91.62 | 5920 | 5920 | N.A. | Expansion Anchors | 4 | 4 - 1/2" anchors | Floor-Mounted/Wall Supported | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | Minor | None | MCC-EC - 4 straps at top welded to steel shear wall. Some failed, base of units slid.
|  |  |  | Electrical Equip. | MCC | 120 | 20 | 91.62 | 4500 | 4500 | N.A. | Expansion Anchors | 4 | 4 - 1/2" anchors | Floor-Mounted/Wall Supported | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | Minor | None | MCC-ED - 4 straps at top welded to steel shear wall. Some failed, base of units slid.
|  |  |  | Electrical Equip. | MCC | 200 | 20 | 91.62 | 7340 | 7340 | N.A. | Expansion Anchors | 6 | 6 - 1/2" anchors | Floor-Mounted/Wall Supported | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1 | - | - | - | - | - | - | 1.25 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | MCC-EF - 6 straps at top
|  |  |  | Electrical Equip. | MCC | 140 | 20 | 91.62 | 5210 | 5210 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1 | - | - | - | - | - | - | 1.25 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | MCC-EG - 4 straps at top
|  |  |  | Electrical Equip. | MCC | 160 | 20 | 91.62 | 2920 | 2920 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1 | - | - | - | - | - | - | 1.25 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | MCC-EH - 4 straps at top
|  |  |  | Electrical Equip. | MCC | 100 | 20 | 91.62 | 3630 | 3630 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1 | - | - | - | - | - | - | 1.25 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | MCC-EJ - 4 straps at top
|  |  |  | Electrical Equip. | MCC | 80 | 20 | 91.62 | 3080 | 3080 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.38 | - | - | - | - | - | - | 1 | - | 0.8 | 0.8 | - | - | - | - | - | - | 1 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | MCC-EK - 4 straps at top
|  |  |  | Electrical Equip. | MCC | 80 | 20 | 91.62 | 3080 | 3080 | N.A. | Expansion Anchors | 2 | 2 - 1/2" anchors | Floor-Mounted/Wall Supported | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | Minor | None | MCC-EL - 4 straps at top welded to steel shear wall. Some failed, base of units slid.
Northridge EQ | (6) | Non-instrumented |  | Mech. Equip. | Steam Generator | 93 | 42 | 52 | 11600 | 11600 | N.A. | Expansion Anchors | 8 | 4 - 1" x 6" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | SG-1, -2. 2 units.
|  |  |  | Mech. Equip. | Heat Recovery Unit | 129 | 106 | 125 | 41210 | 41210 | N.A. | Expansion Anchors | 8 | 4 - 11/4" x 71/4" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | Minor | HRU-1, -2. 2 units. Anchor slip reported
|  |  |  | Mech. Equip. | Auxiliary Burner | 172 | 78 | 92 | 13171 | 13171 | N.A. | Expansion Anchors | 4 | 2 - 1" x 6" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | AB-1, -2. 2 units.
|  |  |  | Mech. Equip. | Continuous Blowdown Nipple | 45 | 21 | 79 | 2300 | 2300 | N.A. | Expansion Anchors | 4 | 2 - 3/4" x 33/8" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | HRHE-1
|  |  |  | Mech. Equip. | Turbine Generators | 306 | 93 | 101 | 51000 | 51000 | N.A. | Expansion Anchors | 22 | 11 - 7/8" x 4" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | GTU-1, -2. 2 units.
|  |  |  | Mech. Equip. | Air Compressor | 72 | 39.5 | 41 | 3100 | 3100 | N.A. | Expansion Anchors | 4 | 2 - 3/4" x 33/8" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | AC-1, -2. 2 units.
|  |  |  | Mech. Equip. | Water Softener | 59 | 29 | 126 | 26500 | 26500 | N.A. | Expansion Anchors | 4 | 2 - 3/4" x 33/8" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | WS-1, -2. 2 units.
|  |  |  | Mech. Equip. | Chillers | 198 | 46 | 188 | 57500 | 57500 | N.A. | Expansion Anchors | 4 | 2 - 11/4" x 71/4" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | CH-1,-2,-3, Chillers (a.k.a. ARUs), 3 units.
|  |  |  | Mech. Equip. | Air Compressor | 39 | 19 | 36 | 2600 | 2600 | N.A. | Expansion Anchors | 4 | 2 - 1/2" x 33/8" anchor each side | Floor-Mounted | Mezzanine | 0.5 (est.) | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | - | - | - | - | - | - | - | - | - | 0.84 (est.) | - | - | - | - | - | - | - | - | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | AC-3. On mezzanine.
|  |  |  | Mech. Equip. | Air Compressor | 40 | 18 | 48 | 1500 | 1500 | N.A. | Expansion Anchors | 4 | 2 - 1/2" x 33/8" anchor each side | Floor-Mounted | Mezzanine | 0.5 (est.) | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | - | - | - | - | - | - | - | - | - | 0.84 (est.) | - | - | - | - | - | - | - | - | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | AC-4,-5. 2 units on mezzanine.
|  |  |  | Mech. Equip. | Domestic Water Heater | 24 | 24 | 104 | 1330 | 1330 | N.A. | Expansion Anchors | 8 | 4 - 5/8" x 23/4" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | DWH-1
|  |  |  | Mech. Equip. | Domestic Water Heater | 24 | 24 | 104 | 1514 | 1514 | N.A. | Expansion Anchors | 8 | 4 - 5/8" x 23/4" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | DWH-2
|  |  |  | Mech. Equip. | Domestic Water Heater | 24 | 24 | 104 | 610 | 610 | N.A. | Expansion Anchors | 8 | 4 - 5/8" x 23/4" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | DWH-3
|  |  |  | Mech. Equip. | Domestic Water Heater | 24 | 24 | 104 | 1416 | 1416 | N.A. | Expansion Anchors | 8 | 4 - 5/8" x 23/4" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | DWH-4
|  |  |  | Mech. Equip. | 2500-gal. Expansion Tank | 66 | 66 | 194 | 20690 | 20690 | N.A. | Expansion Anchors | 8 | 4 - 1" x 81/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | HTW ET
|  |  |  | Mech. Equip. | 1460-gal. Make-up Tank | 38 | 38 | 180 | 12083 | 12083 | N.A. | Expansion Anchors | 4 | 2 - 1" x 61/2" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | HTW MU
|  |  |  | Mech. Equip. | Air Recovery for AC-1, 2 | 42 | 42 | 74 | 3100 | 3100 | N.A. | Expansion Anchors | 2 | 1 - 1/2" x 21/4" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | AR -1, -2
|  |  |  | Mech. Equip. | Air Recovery for Soot Blower | 42 | 42 | 86 | 440 | 440 | N.A. | Expansion Anchors | 6 | 3 - 3/4" x 31/4" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.33 | 0.11 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | AR - SBC
|  |  |  | Mech. Equip. | Cooling Tower | 144 | 52 | 120 | 6850 | 6850 | N.A. | Expansion Anchors | 16 | 8 - 3/4" x 33/8" anchor each side | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | None | CT-4, -5
|  |  |  | Mech. Equip. | Oxygen Tank | 96 (est.) | 96 (est.) | 276 (est.) | 6927 (est.) | 54059 (est.) | N.A. | Cast-in-place Anchors | 3 | 1 - 1" anchor each leg | Floor-Mounted | Ground | 0 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.55 | 0.17 | - | - | - | - | - | - | 0.6 (est.) | 0.6 (est.) | - | - | - | - | - | - | 1 (est.) | - | 0.84 (est.) | 0.84 (est.) | - | - | - | - | - | - | 1 | 0.54 (est.) | - | - | - | - | - | - | - | - | None | None | Major | 6000-gallon vertical liquid oxygen tank. Bolt sheared off (steel failure).
Northridge EQ | (6) | Instrumented |  | Mech. Equip. | Emergency Chiller | 196 (est.) | 72 (est.) | 60 (est.) | 10000 (est.) | 10000 (est.) | N.A. | Vibration Isolator | 6 | Can-internally snubbed | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.75 | 0.25 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | Major | None | Two units. 3/4" bolts between unit and isolator failed. Unit fell from isolator and displaced laterally approximately 6 inches.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 41 | 54 | 1800 | 1800 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.35417 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-11, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 41 | 50 | 1650 | 1650 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.35417 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-12, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 41 | 54 | 1800 | 1800 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.35417 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-21, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 41 | 54 | 1650 | 1650 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.35417 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | None | SF-22, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Fan bearings replaced.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 41 | 54 | 2000 | 2000 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.35417 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | None | SF-31, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Fan bearings replaced.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 41 | 54 | 1650 | 1650 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.35417 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | None | SF-32, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Fan bearings replaced.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 41 | 54 | 1800 | 1800 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.35417 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-41, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 41 | 54 | 1650 | 1650 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.35417 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-42, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 40 | 52 | 2000 | 2000 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-51, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 40 | 52 | 1800 | 1800 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-52, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 39 | 41 | 50 | 1700 | 1700 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-61, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 38.5 | 37 | 49 | 1500 | 1500 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-62, 38 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 27.5 | 33 | 39.5 | 975 | 975 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-65, 23 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 27.5 | 33 | 39.5 | 975 | 975 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-66, 23 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 38 | 36 | 40 | 1350 | 1350 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | Major | SF-71, 34 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Fan bearings replaced. Expansion anchor failure.
|  |  |  | Mech. Equip. | Axial Supply Fan | 38 | 36 | 40 | 1350 | 1350 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-72, 34 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 52 | 39 | 44 | 1500 | 1500 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-75, 38 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 52 | 39 | 44 | 1700 | 1700 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-76, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 41 | 54 | 2000 | 2000 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-81, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 40 | 41 | 54 | 1700 | 1700 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-82, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Supply Fan | 27.5 | 30 | 41 | 750 | 750 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | SF-91, 27 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Return Exhaust Fan | 38.5 | 41 | 118 | 1800 | 1800 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | None | R/EF-13, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Fan bearings replaced.
|  |  |  | Mech. Equip. | Axial Return Exhaust Fan | 39 | 47 | 104 | 1750 | 1750 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | None | R/EF-23, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Fan bearings replaced.
|  |  |  | Mech. Equip. | Axial Return Exhaust Fan | 38.5 | 48 | 114 | 1800 | 1800 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | None | R/EF-33, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Fan bearings replaced.
|  |  |  | Mech. Equip. | Axial Return Exhaust Fan | 38.5 | 40.5 | 117 | 2000 | 2000 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | None | R/EF-43, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Fan bearings replaced.
|  |  |  | Mech. Equip. | Axial Return Exhaust Fan | 38.5 | 33 | 107 | 1750 | 1750 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | Major | R/EF-53, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Anchor Failures.
|  |  |  | Mech. Equip. | Axial Return Exhaust Fan | 37.5 | 37.5 | 116 | 1450 | 1450 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | R/EF-63, 38 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Return Exhaust Fan | 23 | 33 | 124.5 | 975 | 975 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | R/EF-67, 23 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Return Exhaust Fan | 54 | 33.5 | 64.5 | 1250 | 1250 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | Major | R/EF-73, 36 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Fan bearings replaced. Anchor failures.
|  |  |  | Mech. Equip. | Axial Return Exhaust Fan | 54 | 33.5 | 114 | 1300 | 1300 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | Major | R/EF-77, 36 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Anchor Failures.
|  |  |  | Mech. Equip. | Axial Return Exhaust Fan | 38.5 | 33.5 | 115.5 | 1750 | 1750 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | Major | R/EF-83, 45 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Exhaust Fan | 34.5 | 34.5 | 56 | 900 | 900 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | None | EF-14, 34 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Fan bearings replaced.
|  |  |  | Mech. Equip. | Axial Exhaust Fan | 33.5 | 39.5 | 114 | 850 | 850 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | EF-24, 34 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Exhaust Fan | 33.5 | 39.5 | 113.5 | 775 | 775 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | Minor | None | None | EF-34, 34 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform. Fan bearings replaced.
|  |  |  | Mech. Equip. | Axial Exhaust Fan | 33.5 | 28.5 | 115 | 850 | 850 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | 3rd Floor | 0.4 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.6 | - | - | - | - | - | - | 1.5789 | - | 0.8 | 1.015 | - | - | - | - | - | - | 1.2687 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | EF-44, 34 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Exhaust Fan | 33 | 33 | 116 | 775 | 775 | N.A. | Expansion Anchors | 12 | 4 - 3/4" for 2 legs and 2 - 3/4" for 2 legs | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | EF-54, 34 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Exhaust Fan | 23 | 22 | 62.5 | 550 | 550 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | EF-64, 25 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Exhaust Fan | 16 | 19 | 90.5 | 450 | 450 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | EF-68, 23 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Exhaust Fan | 16 | 28 | 82 | 525 | 525 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | EF-74, 23 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Exhaust Fan | 58 | 33.5 | 106 | 900 | 900 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | EF-78, 34 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
|  |  |  | Mech. Equip. | Axial Exhaust Fan | 33.5 | 34 | 112 | 775 | 775 | N.A. | Expansion Anchors | 16 | 4 - 3/4" each leg | Floor-Mounted | Roof | 1 | - | - | - | - | 1976 CAC | - | - | - | - | - | - | - | 0.5 | 0.17 | - | - | - | - | - | - | 0.38 | 0.75 | - | - | - | - | - | - | 1.9737 | - | 0.8 | 1.5 | - | - | - | - | - | - | 1.875 | 0.33 | - | - | - | - | - | - | - | - | None | None | None | EF-84, 34 in. dia. Braced platform w/ 4 legs. Fans supported by 4 vibration isolators on top of platform.
References: | 1. Chen, M.C., Pantoli, E., Wang, X., Astroza, R., Ebrahimian, H., Mintz, S., Hutchinson, T., Conte, J., Restrepo, J., Meacham, B., Kim, J., and Park, H.; 2013. BNCS Report #1: Full-scale structural and nonstructural building system performance during earthquakes and post-earthquake fire – specimen design, construction and test protocol. Structural Systems Research Project Report Series, SSRP 13/9. University of California San Diego, La Jolla, CA.
2. Pantoli, E., Chen, M.C., Wang, X., Astroza, R., Ebrahimian, H., Mintz, S., Hutchinson, T., Conte, J., Restrepo, J., Meacham, B., Kim, J., and Park, H.; 2013. BNCS Report #2: Full-scale structural and nonstructural building system performance during earthquakes and post-earthquake fire – test results. Structural Systems Research Project Report Series, SSRP 13/12. University of California San Diego, La Jolla, CA.
3. Pitman, M., Anagnostopoulou, M., and Filiatrault, A.; 2010. Model PT2 cooling tower with upgraded structure and restrained vibration isolation systems. Structural Engineering and Earthquake Simulation Laboratory, SEESL-2010-02. State University of New York at Buffalo, Buffalo, NY.
4. Phipps, M.; Estructure; Oakland, CA (Note: At the time of the posting of this database, a paper containing the data is under development. When the paper is published, this reference and the spreadsheet will be updated and posted using the same DOI as this version. Periodically recheck this DOI, if you want to review the reference to the paper after it is published.
5. Wilcoski, J.; 2015. U.S. Army ERDC-CERL; (Personal Communications)
6. URS Consultants, Inc.; 1994. Northridge Earthquake Study of Seismic Design Factors for Hospital Non-Structural Components. OSHPD Contract Number 91-5124, Office of Statewide Health Planning and Development, Facilities Development Division, Sacramento, CA
Notes: | [1] NSCS Types: Equipment, Architectural, Contents, and etc.
[2] In the case of single-axis input, H = height, L = length (along primary shaking axis), W = width (transverse to primary shaking axis); and in the case of multiple-axis input H = height, L = length (in EW direction), W = width (in NS direction).
[3] In the case of single-axis input, frequency associated with primary shaking direction; and in the case of multiple-axis input, frequency associated with EW/NS/V.